Town Manager's Report

april 2012

Prepared by David Haller

Streets:

- Staff installed a temporary speed bump on Huntley Circle.

- Staff repaired a number of street lights.

- Staff cleaned East and West Main Street.

- Staff worked with Frederick County Paving to complete a number of paving projects.

Water:

- Rainbow Lake is at the spillway level.

- The roughing filters are being backwashed twice per day and the DE filters are being done once per week.

- Staff has completed water delivery system flushing.

- Our wells are now averaging about 4.5’ below their May 2011 levels.

- Water production and consumption.  We produced and purchased an average of 270,168 GPD.  We consumed an average of 240,930 GPD.

The difference is "Backwash Water" ... (10.8%). We purchased 430,575 gallons of

water from MSM this month.

  - 31.3% of this water came from wells.

  - 5.3% of this water came from Mt. St. Mary's.

  - 63.4% of this water came from Rainbow Lake.

Wastewater:

- The overland flow treatment system is operational for the season.

- The pump station maintenance has been completed.

- We received about 2.6” of precipitation this month (the average is 3.8”).

  - We have a precipitation DEFICIT of 6.5" over the last six months.  The average precipitation for the period from November 1 thru April 30 is 21.5".  We have received 15.0" for that period.

- Wastewater Treatment:

  - We treated an average of 333.000 GPD (consumed 240,930 GPD) which means that 27.6% of the wastewater treated this month was "wild water".

  - We had no spills of untreated sewerage in the month of April.

  - We exceeded the plant’s design capacity on 1 day in the month of April.

04/22	969,000 GPD

Trash:  Trash pickup will remain Mondays for the remainder of the month of May.

Parks:

- Staff performed monthly maintenance in all parks.

- Staff has been working on the ballfields in both Memorial and Community Parks.

- Staff has repaired a water leak in the restroom at the girls softball field.

I Recently Attended the Following Meetings:

- 04/02	Met with a property owner to discuss water service

- 04/05	Met with a  property owner to discuss grease trap ordinance

- 04/11	Met with the mayor to review ongoing operations

- 04/12	met with the mayor and Town Attorney to review and discuss a parks

situation

- 04/12	Attended BOCC/Municipal Meeting

- 04/18	Budget meeting with staff

- 04/19	Met with FEMA staff related to upcoming G-8 conference

- 04/19	Met with the mayor and a church related to a property use change

- 04/23	Met with the mayor, staff and PNC Bank related a bridge loan refinance

- 04/25	Met with the mayor and staff related to budget